Standard Operating Procedure

DG Set Operation

ODISHA MINING CORPORATION LTD.

KODINGAMALI BAUXITE MINE

Authorized By

- PURPOSE:

To provide the standard operating procedure for Diesel Generator operation set in Kodingamali Bauxite Mine.

- SCOPE:

This procedure is applicable for safe Operation of diesel generator in Kodingamali Bauxite Mine.

- RESPONSIBILITY:

|  | Diesel generator | D. G. Operator |
| --- | --- | --- |
|  | D. G. Maintenance | Maintenance Mech. / Ele. Incharge |
|  | Field Operation | Supervisor/Shift Incharge |
|  | Operational Control | Area in-charge |

- SAFETY AND HEALTH HAZARDS:

- Slip/trip/fall.

- Head on Collision.

- Toppling of D G.

- Dust generation during Operation.

- Noise during Operation.

- Vibration during Operation.

- Diesel/ Hydraulic Oil - Inflammable, Fire hazards.

- Acid Batteries- Skin contact can lead to extensive and severe burns and highly toxic.

In order to avoid injuries to personal and damage to machinery, the following precautions are very important.

- Work required PPE i.e. with safety shoes, helmet, dust musk, fluorescent jacket suitable for long distance visibility etc.

- Pre Operation Safety features checklist.

- Regular Checks & Maintenance.

- Use chimney to realize fumes minimum height 5 to 10 mtrs.

- Use 130 DB ear plug/muff.

Note: Report immediately to Supervisor, Shift Incharge and Safety officer for any incident/accident.

- ENVIRONMENT ASPECT:

- Dust generation

- Noise Pollution

- Vibration

- Oil Spillage

Preventive measures:

- Regular use blower for dust control.

- Use of Dust Mask/Earplug

Control of leakages

- TOOLS:

All Work required PPEs like Safety Helmet, Safety shoes, Nose mask, Ear Plug, hand gloves & Jacket.

- PROCEDURE:

Experienced persons should be employed for the job. Ensure that persons running the DG are equipped with safety helmet.

FOR STARTING DIESEL GENERATOR SET IN MANNUAL MODE

- Check fuel level into the diesel service tank.

- Check battery voltage on the alternator panel. It should be 23 to 26 volt DC.

- Check coolant level into the radiator.

- Start lubricating pump by pushing its “ÖN” button on the breaker panel.

- Release the Red Colour Emergency Push button and reset the DG set by pressing the Reset button. Crank the engine by turning the key to “RUN” position.

- Engine will pick-up and will develop voltage.

- Check voltage between R-Y, Y-B and B-R. It should be 415 to 420 volts.

- Check frequency of supply, It should be 49.5 to 50Hz.

- Now close the DG breaker from the alternator panel.

- Use touch screen to scroll the reading.

- Check various readings of parameters on alternator panel and note it in the DG set operation monitoring record.

- The parameters are: RPM, lube oil pressure, lube oil temperature, water temperature

(in / out ), voltage (RY, YB, BR ), current (R, Y, B,) frequency, KWH, KW, P.F.

FOR STOPPING DIESEL GENERATOR SET IN MANUAL MODE

- Check final reading of parameters and note in the DG set log book.

- By pressing open button on the alternator panel release the DG in comer breaker.

- Turn the key of DG set to OFF position.

- Press the red colour Emergency push button.

FOR STARTING DIESEL GENERATOR SET IN AUTO MODE

- After the power failure, the engine will start automatically after 30 seconds.

- Check fuel level into the diesel service tank.

- Check coolant level into the radiator.

- Engine will pick-up and will develop voltage.

- Check voltage between R-Y, Y-B and B-R. It should be 415 to 420 volts.

- Check frequency of supply, It should be49.5 to 50 Hz.

- DG breaker will close automatically.

- Use touch screen to scroll the readings.

- The parameters are: RPM, lube oil pressure lube oil temperature, water temperature (in / out), voltage (RY, YB, BR), current (R, Y, B), Frequency, KWH, KW, PF.

FOR STOPPING DIESEL GENERATOR SET IN AUTO MODE

- DG set verifies the M.S.E.B. Supply is resumed.

- The DG incomer, bus coupler 1 and 2 breakers will open automatically.

- The breaker of transformer 1 and 2 will close automatically.

SHUT DOWN:

- Install the machine in safe place.

- Switch off all apparatus which work on electricity or engine.

- Remove ignition key & lock the cabin.

| PROTOCOL OF DIESEL FILLING |  |  |  |  |
| --- | --- | --- | --- | --- |
| LOCATION: MYTHRI CAMP DG SHED |  |  |  |  |
| FREQUENCY OF FILLING | 2 Time In A Day |  |  |  |
| TIMING OF FILLING | Any Time In A And B Shift |  |  |  |
| MANDATORY AUTHORITY | 1.Mahendra Naik (Electrician) |  |  |  |
|  | 2.Ranjan Ku Jena (Electrician) |  |  |  |
|  | 3.Kabitra Muduli (Electrician) |  |  |  |
| MANDATORY PPEs | 1.Hand Gloves |  |  |  |
|  | 2.Dust Mask |  |  |  |
|  | 3.Helmet |  |  |  |
|  | 4.Refecting Jacket |  |  |  |
|  | 5.Safety Shoe |  |  |  |
| PROCEDURE | 1. Entry Of Loaded Vehicle. ( Diesel Browser ) |  |  |  |
|  | 2. Authorized Person Accompany |  |  |  |
|  | 3. Authorized Person-Proper Compliance Safety Protocol, Follow Do & Don't, Safety Devices Of Vehicle. |  |  |  |
|  | 4. Permission For Loading. |  |  |  |
|  | 5. Close & Exit. |  |  |  |

| DAILY HOUSEKEEPING PROTOCOL |  |
| --- | --- |
| Location: Mythri Camp DG Shed |  |
| Frequency of Cleaning | 1 times |
| Timing of Cleaning | 09 am to 10 am |
| Authorized Cleaning Crew | - Parama Perpeka (helper) |
|  | - Karunakar Benia (helper) |
|  | - Mahendra Naik (electrician) |
|  | - Ranjan Ku Jena (electrician) |
|  | - Kabitra Muduli (electrician) |
| Mandatory PPEs | - Hand Gloves |
|  | - Dust Mask |
|  | - Helmet |
|  | - Reflecting Jacket |
|  | - Safety Shoe |
| Cleaning Procedure | Follow do and don’ts, types of cleaning: general cleaning and dusting. |
| Garbage Segregation Procedure | Dispose in respective dustbins or store house. |
| Garbage Disposal Procedure | Dispose dustbin garbage in disposal pit |
| Miscellaneous Call | Emergency response during miscellaneous cleaning requirement |